Post-Flood Fire Safety Checklist

After a flood, a number of actions should be taken to re-establish the fire safety of the facility. These include:

### Building and Grounds

- Conduct a damage assessment as soon as the area is safe to enter.

- Check for possible washouts that may have undermined roads, buildings, water mains, or gravity tank foundations.

- Provide access to building and grounds by clearing debris from outside areas.

- Check to ensure roads for fire department access are open and undamaged.

- Clear fire exits of debris and floodwater barriers (e.g., sandbags).

- Review emergency evacuation plan and adjust, if needed, to accommodate flood damage.

- Clear fire hydrants of any debris that might hinder access by the fire department.

### Fire Protection Equipment

- Inspect all fire protection equipment for physical damage, including sprinkler heads, valves, and pipes.

- Check sprinkler valves for operation and proper settings.

- Verify water supply pressure is equal to previous reading.

- Perform a main drain test, after fully servicing the automatic sprinkler system.

- If the temperature will fall below freezing, provide temporary heating for the sprinkler system.

- Check fire pump intakes and discharges for obstructions, and clean if necessary.

- Replace fire pump electric motors and overhaul internal combustion motors that have been under water.

- Drain or pump out all valves pits containing water or silt.

- Remove, clean, and dry any fire hoses that were submerged in water.

- Test fire alarm and detection systems for proper operation.

- Inspect and clean all portable extinguishers that have been submerged.

### Flammable and Combustible Liquids and Gases

- Check flammable and combustible liquids or gas containers for damage.

- Check bulk tanks for damage, broken piping, and settling of tank.

### Heating an Electrical Equipment

- Have equipment that has been flooded cleaned, dried out, and the electrical insulation tested.

- Have heating equipment serviced by a qualified technician before returning it to operation.

- Ensure that all cords and equipment used during recovery efforts are listed or approved for wet locations.

- Monitor portable and emergency generator use for carbon monoxide buildup, power back feeds, and improper fueling.